PART 1  	GENERAL

## RELATED WORK

### Lighting Equipment.

## RELATED SECTIONS

### Section 01 33 00 – Submittals.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 26 05 00 – Common Work Results – Electrical.

# PRODUCTS

## Motion Sensors

### Ceiling Sensor:  ultrasonic technology, surface mounted on ceiling, with flush backbox if in finished ceiling area.

#### Power pack in backbox operates at line voltage of lighting circuit.

##### Pack contains output contact to control luminaires on circuit.  Contact rated for voltage of operation of luminaires.

##### Provide ancillary hardware to provide control function as detailed on the drawings for the following:  one sensor control more than one luminaire circuit slave pack) or more than one sensor controlling a Power Pack (slave sensor).

#### Wall Sensor:  passive infrared technology, flush mounted in flush single-gang box in wall by door to room.

##### Controls 120Vac lighting circuit in room; manual-on and auto-off by sensing of infrared energy from a moving human body has ended.

##### Delay-off timer, adjustable time 0.5 to 30 minutes.

##### Motion Sensitivity, adjustable.

##### Manual-on switch.

##### Compatible with electronic ballasts.

##### Colour:  white

# EXECUTION

## INSTALLATION

### Install sensors at locations indicated.

### For ceiling sensors; interconnect sensors and power packs as detailed and to manufacturer’s instructions, and to lighting circuit.

## FIELD QUALITY CONTROL

### Demonstrate that ceiling sensors and power packs control lighting circuits to the intent of the design.

### Demonstrate that wall sensors automatically turn off lighting in room without nuisance off cycles.

### END OF SECTION