# General

## Section Includes

### Control panel.

### Detection Accessories.

### Communications.

### Environmental monitoring.

## Related sections

### Section 01 33 00 – Submittal Procedures.

### Section 01 78 00 – Closeout Submittals.

### Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Section 26 05 00 – Common Work Results - Electrical.

## Reference Standards

### Electronic Industries Association (EIA)

#### REC 12749, Power Supplies.

#### RS 16051, Sound Systems.

### National Fire Protection Association (NFPA)

#### NFPA 70, Article 517, National Electric Code.

#### NFPA 101, Life Safety Code.

### Underwriters Laboratories of Canada (ULC)

#### CAN/ULC-S302, Installation and Classification of Burglar Alarm Systems for Financial and Commercial Premises, Safes and Vaults.

#### CAN/ULC-S303, Local Burglar Alarm Units and Systems.

#### CAN/ULC-S304, Intrusion Detection.

#### CAN/ULC-S306, Intrusion Detection Units.

#### ULC-S318, Power Supplies for Burglar Alarm Systems.

#### ORD-C634, Connectors and Switches for Use with Burglar Alarm Systems.

### Underwriters' Laboratories (UL)

#### UL 603, Standard for Power Supplies For Use With Burglar-Alarm Systems.

#### UL 639, Standard for Intrusion-Detection Units.

## Definitions

### EAC: Electronic Access Control System.

### PIR: Passive Infrared Detectors.

## Design Performance Requirements

### Design intrusion detection system using ULC/UL Listed Alarm Service Company.

### Design system as a modular access control, alarm monitoring system expandable, and easily modified for inputs, outputs and remote control stations.

#### Design components in accordance with CAN/ULC-S306 and be capable of:

##### Annunciating undesirable, abnormal or dangerous condition.

##### Prioritizing alarms by alarm type; i.e. panic/duress, intrusion and tamper.

##### Determining zone where alarm occurred.

##### Annunciating power failure and power restoration.

##### Annunciating low battery condition.

##### Operate continuously for minimum period of 4 hours in the event of a power failure.

### Equip control panels with continuous tamper detection on door and wall.

#### Tamper detection to trigger alarm and trouble light.

### Design system with:

#### Alarm masking.

#### Remote maintenance or diagnostics with password activation and call back modem.

#### Unique identifier for each authorized person.

#### Arming and disarming capabilities: manual and automatic by time of day, day of week, or by operator command.

#### Support both manual and automatic responses to alarms entering system.

#### Each alarm capable of initiating different functions of camera, homing, and activation of remote devices, audio switching, door control and card or pin validation.

#### Zone or alarm location annunciated at monitoring station.

### Communications link: security level of I as described in CAN/ULC-S304.

### Signal link: Security level of I as described in CAN/ULC-S304.

### Alarm condition: Design system to provide maximum time for an alarm to be communicated of 60 seconds from alarm initiation to annunciation at remote monitoring location.

### Junction boxes: tamper proof with continuous tamper-detection capability.

### Design system power supplies rated to provide cumulative load of all systems components plus safety factor of 50% or greater.

## Submittals

### Product Data: Submit manufacturer's printed product literature, specifications and datasheet.

#### Submit two copies of WHMIS SDS - Safety Data Sheets.

#### Submit manufacture's literature for each control panel and detection accessory device.

#### Submit:

##### Functional description of equipment.

##### Technical data for all devices.

##### Device location plans and cable lists.

##### Devices mounting location detail drawings.

##### Typical devices connection detail drawings

### Submit shop drawings to indicate project layout, mounting heights and locations, wiring diagrams, detection device coverage patterns and contact operating gaps.

### Submit zone layout drawing indicating number and location of zones and areas covered.

### Submit one sample of each control panel and detection device accessory. Reviewed and accepted control panel, detection device accessory will be returned for incorporation into work.

### Test Reports: Submit certified test reports from approved independent testing laboratories indicating compliance with specifications for specified performance characteristics and physical properties.

### Certificates: Submit certificates signed by manufacturer certifying that materials comply with specified performance characteristics and physical properties.

#### Submit UL Product Safety Certificates.

#### Submit verification Certificate that service company is ULC/UL List alarm service company.

#### Submit verification Certificate that intrusion alarm system is Certified Alarm System.

### Instructions: Submit manufacturer's installation instructions.

### Manufacturer's Field Services: Submit copies of manufacturer's field reports.

### Maintenance Data: Submit maintenance data for incorporation into manual specified in Section 01 78 00 - Closeout Submittals.

#### Include:

##### System configuration and equipment physical layout.

##### Functional description of equipment.

##### Instructions of operation of equipment.

##### Illustrations and diagrams to supplement procedures.

##### Operation instructions provided by manufacturer.

##### Cleaning instructions.

## Warranty

### Manufacturer’s Warranty:  Submit, for Owner’s acceptance, manufacturer’s warranty document executed by authorized company official, stating that the Intrusion Detection system is warranted against defects in operation, material and workmanship for a period of 12 months from date of substantial completion of the project.

## Support Services

### Provide manufacturer/dealer advice, information and support services for 1 year.

## TRAINING

### Arrange and pay for on-site lectures and demonstrations by system manufacturer to train operational personnel in the use and maintenance of the system.

# Products

## Materials

### Control Panel: ULC approved, expandable and designed for multiplexed expansion.

#### Zones (protection inputs): 8.

#### Fixed Zones: 8.

#### Expandable: 8 - 32 zones.

#### Number of user codes required: 10.

#### Number of Areas/Partitions required: 10.

#### Keypads: LCD (liquid crystal display).

#### Alarm:  Monitored.

#### System: Wired.

#### Integrated with sub systems.

#### Number of programmable outputs required: 5.

#### System supervision: telephone line, battery, and AC power.

#### Siren output.

#### Number of devices per zone: as required.

### Detection Accessories:

#### Passive Infrared Detectors (PIR's): ULC approved, digital.

##### Coverage pattern: as required/indicated.

##### Temperature requirement: as required/indicated.

##### Tamper switch.

##### Mounting: wall or ceiling.

#### Glassbreak Detector: ULC approved, complete with tamperproof switch and be designed to meet temperature and mounting requirements of project.

##### Coverage pattern: as required/indicated.

#### Dual Passive Infrared and Microwave: ULC approved, complete with tamperproof switch, and be designed to meet temperature and mounting requirements of project.

##### Coverage pattern: as required/indicated

#### Contacts: ULC approved.

##### Mounting: surface.

##### Mounting locations: door window or overhead door.

##### Operating gap: 9.5 mm.

##### Security level: high security

##### Type: magnetic biased.

#### Vibration or Shock Sensors: as required.

#### Photo Electric Beams: as required.

#### Notification Devices:

##### Siren: 15 watt.

##### Speaker complete with driver voice annunciator.

### Communications: telephone line Digital Dialer.

### Environmental Monitoring: Design system for detection of Smoke/Heat, Temperature Humidity and Flood.

### Connectors and switches: to ORD-C634.

### Power supplies: to ULC-S318 or UL 603.

# Execution

## Manufacturer's Instructions

### Compliance: Comply with manufacturer's written data, including product technical bulletins, product catalog installation instructions, product carton installation instructions, and datasheet.

## Installation

### Install panels, intrusion detection system and components in accordance with manufacturer's written installation instructions to locations, heights and surfaces shown on reviewed shop drawings.

### Install panels, intrusion detection system and components secure to walls, ceilings or other substrates.

### Install required boxes in inconspicuous accessible locations.

### Conceal conduit and wiring.

## Field Quality Control

### Manufacturer's Services:

#### Have manufacturer of products, supplied under this Section, review Work involved in the handling, installation/application, protection and cleaning, of its products and submit written reports, in acceptable format, to verify compliance of Work with Contract.

#### Manufacturer's Field Services: Provide manufacturer's field services consisting of product use recommendations and periodic site visits for inspection of product installation in accordance with manufacturer's instructions.

#### Schedule site visits, to review Work, at stages listed:

##### After delivery and storage of products, and when preparatory Work, or other Work, on which the Work of this Section depends, is complete but before installation begins.

##### During progress of Work at 25% and 60% complete.

##### Commissioning of the Work.

#### Obtain reports, within three (3) working days of review, and submit, immediately, to Owner.

## Verification and commissioning

### Perform verification inspections and test in the presence of Owner.

#### Provide all necessary tools, ladders and equipment.

#### Ensure appropriate subcontractors, and manufacturer's representatives and security specialists are present for verification.

### Visual verification: Objective is to assess quality of installation and assembly and overall appearance to ensure compliance with Contract Documents. Visual inspection to include:

#### Sturdiness of equipment fastening.

#### Non-existence of installation related damages.

#### Compliance of device locations with reviewed shop drawings.

#### Compatibility of equipment installation with physical environment.

#### Inclusion of all accessories.

#### Device and cabling identification.

#### Application and location of ULC approval decals.

### Technical verification: Purpose to ensure that all systems and devices are properly installed and free of defects and damage. Technical verification includes:

#### Measurements of coverage patterns

#### Connecting joints and equipment fastening.

#### Compliance with manufacturer's specification, product literature and installation instructions.

### Operational verification: Purpose to ensure that devices and systems' performance meet or exceed established functional requirements. Operational verification includes:

#### Operation of each device individually and within its environment.

#### Operation of each device in relation with programmable schedule and or/specific functions.

## Cleaning and adjusting

### Remove protective coverings from control panels, detection accessories and components.

### Adjust all components for correct function.

END OF SECTION