# GENERAL

## RELATED WORK

### Section 01 33 00 - Submittal Procedures.

### Section 01 78 00 - Closeout Procedures.

### Section 01 91 13.13 - Commissioning (Cx) Requirements.

### Section 26 05 00 - Common Work Results - Electrical.

### Section 26 05 21 - Wires and Cables (0 - 1000 V).

### Section 26 05 34 - Conduits, Conduit Fastenings and Conduit Fittings.

### Section 28 16 00 - Intrusion Detection.

## REFERENCES

### CSA C22.1, Canadian Electrical Code, Part 1, Safety Standard for Electrical Installations.

### Government of Canada

#### NBC, National Building Code of Canada, latest edition.

### Underwriter’s Laboratories of Canada (ULC)

#### CAN/ULC-S524, Installation of Fire Alarm Systems.

#### ULC-S525, Audible Signal Appliances for Fire Alarm.

#### CAN/ULC-S526, Visual Signal Appliances, Fire Alarm.

#### CAN/ULC-S527, Control Units, Fire Alarm.

#### CAN/ULC-S528, Manual Pull Stations.

#### CAN/ULC-S529, Smoke Detectors, Fire Alarm.

#### CAN/ULC-S530, Heat Actuated Fire Detectors, Fire Alarm.

#### CAN/ULC-S536, Inspection and Testing of Fire Alarm Systems.

#### CAN/ULC-S537, Verification of Fire Alarm Systems.

## SYSTEM DESCRIPTION

### Fully supervised, microprocessor-based, remote monitored fire alarm system, utilizing digital techniques for data control and multiplexing techniques for data transmission.

### System to carry out fire alarm and protection functions; including receiving alarm signals: initiating general alarm; supervising components and wiring; actuating auxiliary functions; initiating trouble signals and signaling to central monitoring system.

### Zoned, non-coded single stage.

### Modular in design to allow for future expansion.

### Operation of system shall not require personnel with special computer skills.

### System to include:

#### Central Control Unit in separate enclosure with power supply, stand-by batteries, central processor with microprocessor and logic interface, main system memory, input-output interfaces for alarm receiving, annunciation/display, and program control/signaling.

#### Power supplies.

#### Initiating/input circuits.

#### Output circuits.

#### Auxiliary circuits.

#### Wiring.

#### Manual and automatic initiating devices.

#### Audible and visual signaling devices.

#### End-of-line resistors.

#### Local and Remote annunciators.

#### Historic event recorder.

#### Drill button on main panel.

## REQUIREMENTS OF REGULATORY AGENCIES

### System:

#### Subject to Provincial Fire Commissioner’s approval.

#### Subject to FC inspection for final acceptance.

#### To electrical inspection approval.

### System components: listed by ULC and comply with applicable provisions of National Building Code and meet requirements of local authority having jurisdiction.

## SUBMITTALS

### Include:

#### Detail assembly and internal wiring diagrams for control unit.

#### Details for devices.

#### Details and performance specifications for control, annunciation and peripherals with item by item cross reference to specification for compliance.

#### Step-by-step operating sequence, cross referenced to logic flow diagram.

## CLOSEOUT SUBMITTALS

### Provide operation and maintenance data for fire alarm system for incorporation into manual specified in Section 01 78 00- Closeout Submittals.

### Include:

#### Instructions for complete fire alarm system to permit effective operation and maintenance.

#### Technical data - illustrated parts list with parts catalogue numbers.

#### Copy of approved shop drawings with corrections completed and marks removed except review stamps.

#### List of recommended spare parts for system.

#### Verification Certificate and Report to CAN/ULC-S537.

## MAINTENANCE MATERIALS

### Provide the following maintenance materials:

#### Two (2) spare audible signal devices.

#### Two (2) spare visual signal devices.

#### Two (2) spare manual pull stations.

#### Two (2) spare thermal detectors.

#### Two (2) spare smoke detectors.

## MAINTENANCE

### Provide one year, s free maintenance from date of substantial completion with two inspections by manufacturer during warranty period and following occupancy.  Inspection tests to conform to CAN/ULC-S536.  Submit inspection report to Owner.

## TRAINING

### Provide on-site lectures and demonstration by fire alarm equipment manufacturer to train operational personnel in use and maintenance of fire alarm system.

## warranty

### Provide manufacturer produce warranty against defects in operation, material and workmanship for 2 years from date of substantial completion.

## VERIFICATION

### The fire alarm system shall be verified to CAN/ULC-S537. A completed and signed verification Certificate shall be provided by the fire alarm system manufacturer’s certified technician/company. The installation technician shall be approved by the AHJ. The verification certificate shall be accompanied with the completed and signed CAN/ULC-S537 Verification Report. The system will not be considered verified until both the CAN/ULC-S537 Certificate and the CAN/ULC-S537 Report are completed and submitted to the Owner. The system shall be free from all deficiencies prior to final verification.

### The verification report shall include a detailed list of all the installed system components, including manufacturer and model numbers for each connected device.

# PRODUCTS

## MATERIALS

### Equipment and devices: ULC listed and labeled and supplied by single manufacturer.

### Power supply: to CAN/ULC-S524.

### Audible signal devices: to ULC-S524.

### Visual signal devices: to CAN/ULC-S526.

### Control unit: to CAN/ULC-S527.

### Manual pull stations: to CAN/ULC-S528.

### Thermal detectors: to CAN/ULC-S530.

### Smoke detectors: to CAN/ULC-S529.

## SYSTEM OPERATION: SINGLE STAGE

### Actuation of any alarm initiating device to:

#### Cause electronic latch to lock-in alarm at central control unit.

#### Indicate zone of alarm at central control unit.

#### Cause audible signaling devices to sound continuously throughout building and at central control unit.

#### Transmit signal to monitoring agency via alarm panel.

#### Cause air conditioning and ventilation units to shut down.

### Acknowledging alarm: indicated at central control unit.

### Possible to silence signals by (alarm silence( switch at control unit, after 60 second period of operation.

### Subsequent alarm, received after previous alarm has been silenced, to re-activate signals.

### Actuation of supervisory devices to:

#### Cause electronic latch to lock-in supervisory state at central control unit.

#### Indicate respective supervisory zone at central control unit.

#### Cause audible signal at central control unit to sound.

#### Activate common supervisory sequence.

### Resetting alarm or supervisory device not to return system indications/functions back to normal until control unit has been reset.

### Trouble on system to:

#### Indicate circuit in trouble at central control unit.

#### Activate “system trouble” indication, buzzer and common trouble sequence.  Acknowledging trouble condition to silence audible indication; whereas visual indication to remain until trouble is cleared and system is back to normal.

### Trouble on system to be suppressed during course of alarm.

### Trouble condition on any circuit in system not to initiate any alarm conditions.

## CONTROL PANEL

### Central control unit (CCU).

#### Suitable for DCLA communication style: to CAN/ULC - S524.

#### Features specified are minimum requirements for microprocessor-based system with digital data control and digital multiplexing techniques for data transmission.

#### Minimum capacity of 250 addressable monitoring and 250 addressable control/signal points.

#### System to provide for priority reporting levels, with fire alarm points assigned highest priority, supervisory and monitoring lower priority, and third priority for troubles.  Possible to assign control priorities to control units in system to guarantee operation or allow emergency override as required.

#### Integral power supply, battery charger and standby batteries.

#### Basic life safety software: retained in non-volatile Erasable Programmable Read-Only-Memory (EPROM).  Extra memory chips: easily field-installed.  Random-Access Memory (RAM) chips in panel to facilitate password-protected field editing of simple software functions (e.g. zone labels, priorities) and changing of system operation software.

#### Circuitry to continuously monitor communications and data processing cycles of microprocessor.  Upon failure, audible and visual trouble indication to activate.

#### Support up to 2 RS-232-C I/O ports.  CCU output: parallel ASCII.

#### Equipped with software routines to provide Event-Initiated-Programs (EIP); change is status of one or more monitor points, may be programmed to operate any or all of system, s control points.

#### Software and hardware to maintain time of day, day of week, day of month, month and year.

## POWER SUPPLIES

### 120 V, 60 Hz as primary source of power for system.

### Voltage regulated, current limited distributed system power.

### Primary power failure or power loss (less than 102 V) will activate common trouble sequence.

### Interface with battery charger and battery to provide uninterruptible transfer of power to standby source during primary power failure or loss.

### During normal operating conditions fault in battery charging circuit, short or open in battery leads to activate common trouble sequence and standby power trouble indicator.

### Standby batteries: sealed, maintenance free.

### Continuous supervision of wiring for external initiating and alarm circuits to be maintained during power failure.

## INITIATING/INPUT CIRCUITS

### Receiving circuits for alarm initiating devices such as manual pull stations, smoke detectors, and heat detectors wired in DCLA configuration to central control unit.

### Alarm receiving circuits (active and spare): compatible with smoke detectors and open contact devices.

### Actuation of alarm initiating device: cause system to operate as specified in ”System Operation“.

### Receiving circuits for supervisory, N/O devices.  Devices: wired in DCLA configuration to central control unit.

### Actuation of supervisory initiating device: cause system to operate as specified in ”System Operation“.

## ALARM OUTPUT CIRCUITS

### Alarm output circuit: connected to signals, wired in class B configuration to central control unit.

#### Signal circuits operation to follow system programming; capable of sounding horns continuously.  Each signal circuit: rated at 2 A, 24 V DC; fuse-protected from overloading/overcurrent.

### Manual alarm silence, automatic alarm silence and alarm silence inhibit to be provided by system’s common control.

## AUXILIARY CIRCUITS

### Auxiliary contacts for control functions.

### Actual status indication (positive feedback) from controlled device.

### Alarm or supervisory trouble on system to cause operation of programmed auxiliary output circuits.

### Upon resetting system, auxiliary contacts to return to normal or to operate as pre-programmed.

### Auxiliary circuits: rated at 2 A, 24 V DC or 120 V AC, fuse-protected.

### Auxiliary contacts for shut down of all ventilation/exhaust units indicated.

### Auxiliary contacts for release of hold-open devices and roll up shutters.

## WIRING

### Multi-conductor cable assemblies with dedicated bonding wire CSA FAS105 and FT-4 rated.

### To initiating circuits: 16 AWG minimum, or in accordance with manufacturer’s requirements where exceeds minimum.

### To signal circuits: 14 AWG minimum, or in accordance with manufacturer’s requirements where exceeds minimum.

### To control circuits: 14 AWG minimum, or in accordance with manufacturer’s requirements where exceeds minimum.

### Fire alarm cables to be run in EMT conduit unless otherwise noted.

## MANUAL ALARM STATIONS

### Addressable manual pull station.

#### Pull lever, break glass rod, semi-flush wall mounted type, single action, single stage, electronics to communicate station’s status to addressable module/transponder over 2 wires and to supply power to station. Station address to be set on station in field.

## AUTOMATIC ALARM INITIATING DEVICES

### Addressable thermal fire detectors, combination fixed temperature and rate of rise, non-restorable fixed temperature element, self-restoring rate of rise, fixed temperature 57EC, rate of rise 8.3 EC per minute.

#### Electronics to communicate detector’s status to addressable module/transponder.

#### Detector address to be set on detector in field.

### Addressable thermal fire detector, fixed temperature, non-restorable, rated 57EC.

#### Electronics to communicate detector’s status to addressable module/transponder.

#### Detector address to be set on detector in field.

### Addressable variable-sensitivity smoke detectors.

#### Photo-electric type.

#### Electronics to communicate detector’s status to addressable module/transponder.

#### Detector address to be set on detector in field.

### Addressable thermal fire detector, fixed temperature, non-restorable, rated 57EC constructed of moisture proof design.

#### Electronics to communicate detector’s status to addressable module/transponder.

#### Detector address to be set on detector in field.

### Sensitivity settings: 3 settings, determined and operated by control panel.  No shifting in detector sensitivity due to atmospheric conditions (dust, dirt) within certain parameters.

### Ability to annunciate minimum of 2 levels of detector contamination automatically with trouble condition at control panel.

## AUDIBLE SIGNAL DEVICES

### Vibrating horn: semi-flush mounted, red enamel, 24 V DC, 94 dB.

### Exterior horns to be weatherproof design mounted in PVC yard hood.

## VISUAL ALARM SIGNAL DEVICES

### Strobe: flashing white, 24 V dc semi-flush mounted in finished areas.

## END-OF-LINE DEVICES

### End-of-line devices to control supervisory current in signaling circuits sized to ensure correct for each circuit.  Open, short or ground fault in any circuit will alter supervisory current in that circuit, producing audible and visible alarm at main control panel and remotely as indicated.

## ADDRESSABLE CONTROL/MONITOR MODULES

### Addressable modules with address set in field for control/monitoring of external circuits.

### Applications: ventilation unit shut down, sprinkler device monitoring, control of magnetic door hold open devices, door electric strikes, interface to electronic door hardware controllers to facilitate door control functions when required.

### Ensure that control circuits connected to addressable relay dry contacts are protected by fuse to limit current within manufacturer’s requirements.

## AS-BUILT RISER DIAGRAM

### Fire alarm system riser diagram: in glazed frame minimum size 600 x 600 mm.

### Provide complete riser diagram indicating all devices in relative position on communications loop.  Indicate location of each device by Block reference and room name and number.

### Locate riser diagram in main electrical room.

## ISOLATION MODULES

### Isolation modules for segmenting of fire alarm detection loop as indicated.

## PASSIVE GRAPHIC DISPLAY

### Provide passive graphic display, to be mounted adjacent to the main fire alarm control panel.  Plastic laminate type, black artwork on white background, framed under glass approximately size: 600 x 600 mm.

## REMOTE ANNUNCIATOR

### LCD type annunciator providing information as per display on control panel display, to be located in main lobby of building.

## WIRE GUARDS

### Provide factory manufactured wire guards in gymnasium for protection of manual pull stations, fire detectors, strobe lights and alarm horns.

## REMOTE MONITORING

### Provide remote monitoring of fire alarm status to monitoring agency.  Retain services of intrusion alarm service representative for connection to and programming of intrusion alarm control panel to accommodate alarm from fire alarm system.  Include all charges in Division 26 Electrical Contract.

# EXECUTION

## INSTALLATION

### Install systems in accordance with National Building Code of Canada, Canadian Electrial Code CSA-C22.1 and CAN/ULC-S524.

### Installer shall review and comply with fire alarm system manufacturer’s installation requirements where these requirements exceed minimum code requirements.

### Run all fire alarm wiring in conduit.

### A separate bond wire shall be run in all conduits and connected at each junction point.

### Install central control unit and connect to ac power supply.

### Install manual alarm stations and connect to alarm circuit wiring.

### Locate and install detectors and connect to alarm circuit wiring.  Do not mount detectors within 1 m of air outlets.  Maintain at least 600 mm radius clear space on ceiling, below and around detectors.  Locate duct type detectors in straight portions of ducts.

### Connect alarm circuits to main control panel.

### Install horns and visual signal devices and connect to signaling circuits.

### Connect signaling circuits to main control panel.

### Install end-of-line devices at end of signaling circuits.

### Install wiring to ventilation units as identified for shut down under alarm conditions.

### Splices are not permitted.

### Provide necessary raceways, cables and wiring to make interconnections to terminal boxes, annunciator equipment and CCU, as required by equipment manufacturer.

### Ensure that wiring is free of opens, shorts or grounds, before system testing and handing over.

### Identify circuits and other related wiring at central control unit, annunciators, and terminal boxes.

### Connect fire alarm control panel to intrusion alarm control panel for remote monitoring.

### Install factory wire guards in gymnasium on pull stations, fire detectors, strobes and fire alarm horns.

### Install remote annunciator and connect to main control panel.

## FIELD QUALITY CONTROL

### Perform tests in accordance with Section 26 05 00 – Common Work Results - Electrical and Section 01 91 13.13 – Commissioning (Cx) Requirements.

### Fire alarm system:

#### Test each device and alarm circuit to ensure manual stations, thermal and smoke detectors transmit alarm to control panel and actuate general alarm and ancillary devices.

#### Check annunciator panels to ensure alarms are shown correctly.

#### Simulate grounds and breaks on alarm and signaling circuits to ensure proper operation of system.

#### Addressable circuits system style DCLA:

##### Test each conductor on all DCLA addressable links for capability of providing 3 or more subsequent alarm signals on each side of single open-circuit fault condition imposed near midmost point of each link.  Operate Acknowledge/Silence switch after reception of each of the 3 signals.  Correct imposed fault after completion of each series of tests.

##### Test each conductor on all DCLA addressable links for capability of providing 3 or more subsequent alarm signals during ground-fault condition imposed near midmost point of each link.  Operate Acknowledge/Silence switch after reception of each of the 3 signals.  Correct imposed fault after completion of each series of tests.

### Provide final PROM program re-burn for system incorporating program changes made during construction.

### Provide programming for system to provide identification of alarm and trouble conditions to satisfaction of the owner.  Coordinate with the owner prior to programming display items.

END of Section