# General

## SECTION INCLUDES

### Materials and installation for providing a complete water well.

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 - Construction/Demolition Waste Management And Disposal.

## MEASUREMENT PROCEDURES

### Mobilization and demobilization lump sum.

### Measure drilling in unconsolidated formation in metres of each size hole drilled.

### Measure drilling in consolidated formation in metres of each size hole drilled.

### Measure supply and installation of casing in metres of each type and size of casing permanently installed.

### Supply and installation of screen will be lump sum.

### Measure gravel packing in kilograms of gravel installed in well.

### Measure grouting in cubic metres of grout installed in well.

### Measure well development in hours during which contractor is actually engaged in well development.

### Disinfection of well will be lump sum.

### Measure test pumping, including water sampling, in hours during which pump is in operation to successfully complete a test.

### Measure well abandonment in metres of depth.

## REFERENCES

### American National Standards Institute (ANSI)

#### ANSI/AWWA A100, Water Wells.

#### ANSI/AWWA C200, Water Pipe, 6 in. (150 mm) and Larger, Steel.

#### ANSI/AWWA C654, Disinfection of Wells.

### American Society for Testing and Materials International, (ASTM)

#### ASTM B124/B124M, Standard Specification for Copper and Copper Alloy Forging Rod, Bar, and Shapes.

#### ASTM A53/A53M, Standard Specification for Pipe, Steel, Black and Hot Dipped, Zinc Coated, Welded and Seamless.

#### ASTM F480, Standard Specification for Thermoplastic Water Wall Casing Pipe and Couplings Made in Standard Dimension Ratios (SDR), Sch 40 and Sch 80.

### Canadian Standards Association (CSA International)

#### CSA A3000, Cementitious Materials Compendium.

## DEFINITIONS

### Annular space: space between well casing and borehole wall.

### Aquifer: part of formation or group of formations that is water bearing.

### Available drawdown: difference in elevation between static level and top of screen, or between static level and 2 m above bottom of well in case of wells with no screen.

### Consolidated formation: a geologic formation of bedrock.

### Development: application of appropriate techniques to bring well to maximum production capacity and control concentration of suspended solids.

### Drawdown: difference in elevation, between static level and pumping level.

### Perennial yield: maximum rate of flow that could be sustained when pumping well at constant rate for period of 7 log cycles on time/drawdown chart (approximately 19 years).

### Potable water: water that is safe for human consumption.

### Pumping level: difference in elevation between well datum and water level when well is being pumped at stated L/s rate.

### Recovery: time taken for water level to return from pumping level to static level after pumping stops.

### Specific capacity: ratio of pumping rate to drawdown, expressed in L/s.m of drawdown.

### Static level: difference in elevation between well datum and level of water in well when no pumping has been conducted for at least 6 hours.

### Unconsolidated formation: geologic formation of sand, gravel or other soil strata.

### Well datum: top of outer casing or similar fixed point of well head with elevation tied to geodetic or suitable local datum.

## SYSTEM DESCRIPTION

### Work under this section includes construction of one production water well with desired yield of 1.3 L/s extending to depth of approximately 100 m in accordance with ANSI/AWWA A100.

## SUBMITTALS

### Submittals in accordance with Section 01 33 00 - Submittal Procedures.

### On completion of Work, submit to Owner, report containing:

#### Log of well drilling.

#### Geophysical logs.

#### Record drawing of well including:

##### Elevations.

##### Size and length of each casing section installed.

##### Grouting details.

##### Description of screen.

##### Gravel packing details.

#### Records of static water level measurements, times at which they were taken and any observable changes in static water level with well depth.

#### Results of interim and final pumping tests.

#### Well development data.

#### Results of testing of water sample for suspended solids, chemical and bacteriological content.

#### Recommendations on water treatment.

#### Type and size of permanent well pump recommended.

#### Well maintenance instructions.

## QUALIFICATIONS

### Hire services of hydrogeologist, approved by Owner, to advise on well construction and materials.

## WASTE MANAGEMENT AND DISPOSAL

### Separate waste materials for reuse and recycling in accordance with Section 01 74 21 - Construction/Demolition Waste Management and Disposal.

### Remove from site and dispose of packaging materials at appropriate recycling facilities.

### Collect and separate for disposal paper, plastic, polystyrene, corrugated cardboard packaging material in appropriate on-site bins for recycling in accordance with Waste Management Plan.

### Divert unused metal and wiring materials from landfill to metal recycling facility as approved by Owner.

### Divert unused concrete/cement materials from landfill to local facility as approved by Owner.

### Divert unused aggregate materials from landfill to facility for reuse as approved by Owner.

### Fold up metal banding, flatten and place in designated area for recycling.

## PROJECT CONDITIONS

### Before commencing drilling, determine if area in which well is to be drilled has history of flowing wells or natural gas formations.

# Products

## Permanent well casing

### Casing to ASTM A53.

#### Internal diameter: 150 mm.

#### Wall thickness: Schedule 40.

### Use pipe fittings of same standard as pipe casing.

### Joints: welded.

## SCREEN

### To Owner’s approval after analysis of aquifer by hydrogeologist.

### Well screen diameter, length, materials type and openings as recommended.

### Couplings to connect screen sections, when required, to be of same material as screen.

### Provide screen with bail plug, self closing valve, threaded plate or quick setting concrete plug to close bottom.

### Provide screen with neoprene seal at top.

### Join screen to casing by welding.

# Execution

## DRILLING

### Use drilling equipment, methods, fluids and additives approved by Owner’s.

### Drill in locations and to depths to achieve desired flow rate.

### Drill holes plumb and straight.

### Dispose of drill cuttings as directed by Owner.

### Ensure drilling methods do not impair production from aquifers encountered.

### Prevent foreign matter from entering bore hole and prevent contaminated water or other objectionable fluids from reaching aquifer through bore hole.

### Cover top of bore hole to prevent tampering and eliminate dangerous conditions for persons or animals in area.

### Maintain log of bore holes including following information:

#### Depth of changes in formation.

#### Description of formations encountered.

#### Elevations at which aquifers are encountered, sudden changes in water level, loss of drilling fluid or other indications of permeable strata.

#### Electric logging test results.

### In unconsolidated formations, obtain duplicate soil samples from each 3 m of depth drilled and at least one set of duplicate samples from each formation encountered. Submit samples to Owner with identification data on drill hole and depth.

### Obtain continuous samples for at least 7.0 m through aquifer to be screened using split spoon sampling or other method approved by Owner.

### In consolidated formation, obtain one rock sample from each 6.0 m of depth drilled.

### Conduct well development and pumping tests, and obtain clear water samples as directed by Owner.

### Be prepared to control, shut off and seal hole should flowing artesian water or gas be encountered.

### Equip arterial wells with variable flow control device to control rate of flow after completion. Stop flow of water for period of not less than 48 hours by closing control device, and determine if well is effectively sealed to prevent escape of water from annular space of well and its' immediate vicinity. Seal off water by grouting as necessary.

### Seal abandoned holes by approved methods with concrete, cement bentonite grout, or other material approved by Owner.

### Redrill holes lost due to caving or abandoned due to loss of drilling equipment at no cost to Owner.

## SCREEN INSTALLATION

### When aquifer material has been sampled and analyzed, Owner to be advised on type and size of screen required.

### Install screen to manufacturer's recommendations.

## PERMANENT CASING INSTALLATION

### Clean casing pipe and fittings prior to installation.

### Install permanent well casing to sizes and depths as directed by hydrogeologist.

### Centre casing by use of centreing brackets spaced maximum 15 m apart and install so that variance from vertical does not exceed two thirds internal diameter of casing per 30 m of depth.

### Prove alignment by lowering straight section of pipe 12 m long, with outside diameter maximum 12 mm smaller than internal diameter of casing being tested, into casing. If plumb fails to move freely through casing to lowest anticipated pumping level, correct alignment.

### Seal annular space between casing and borehole wall by grouting, to prevent entrance of surface water or other deleterious matter into aquifer, and to prevent intermixing of water.

### After grouting is completed, cut off casing squarely and neatly, maximum 450 mm above ground level and minimum 600 mm above highest recorded flood level. Cover casing with flanged cap to approval of Owner.

### Maintain accurate records of casing lengths and sizes installed.

## GRAVEL PACKING

### Gravel used for gravel packing to be clean, rounded, water washed quartz or granitic gravel free of silt, clay and other deleterious materials.

#### Gradation to be specified by Owner after analysis of aquifer samples.

#### Relative density (formally specific gravity): minimum 2.5.

#### Thin, flat and elongated particles: maximum 2% by mass.

### Place gravel packing as indicated by approved methods acceptable to Owner.

### Store gravel packing in manner which avoids contamination.

## GROUTING AND SEALING

### Seal casing of well extending into consolidated formation into upper 1.5 m of formation by grouting with neat cement grout.

### Drive steel casing into consolidated formation until seal is obtained.

### Fill annular space below 3.0 m depth as indicated.

### Grout annular space from ground surface to 3.0 m depth using neat cement grout, sand cement grout or bentonite.

#### Neat cement grout to be mixture of Type10 Portland cement with maximum 8% by mass bentonite clay and 2% calcium chloride added and water in ratio of 19 L of water per 42.6 kg bag of cement.

#### Sand cement grout to consist of mixture of 2 parts by mass sand to 1 part Portland cement, and with maximum 22.7 water per 42.6 kg bag of cement.

### Place grout from bottom up by methods approved by Owner. Place grout in one continuous operation with entire amount placed before initial set occurs].

### Use retainer, packer or plug at bottom as necessary to ensure grout does not leak into well.

### When further drilling is required after grouting, do not drill until 72 hours after complete placement of grout.

## DISINFECTION

### After well has been completely constructed, thoroughly clean of foreign substances, including tools, timbers, rope, cement, oil, grease, joint dope and scum. Thoroughly swab casing pipe using alkalis if necessary to remove oil, grease or joint dope.

### Disinfect well in accordance with ANSI/AWWA C654.

## TEST PUMPING

### Equipment requirements:

#### Pump with variable pumping rate up to capacity of at least 1.3 L/s and capable of operating a minimum of 54 h without interruption.

#### Discharge piping of sufficient size and length to conduct water being pumped during test to approved point of discharge where it will not recharge aquifer, damage property or create nuisance and equipped with valve close to pump.

#### Apparatus to measure rate of pump discharge to be orifice plate with transparent tube to measure water head upstream of plate, or suitable water metre.

#### Apparatus to measure pumping level to be electric sounder or calibrated air line]

### Conduct interim test pumping during construction as directed by Owner.

### Develop well, if necessary, to optimize yield.

### Final test pumping as follows:

#### Pumping rate as specified.

#### Testing time of 48.

#### After pumping begins, record water level in well at following intervals: every minute for first 10 min, every 2 min for next 10 min, every 5 min for next 40 min, every 10 min for next 1 h, every 30 min for next 3 h, every hour for next 5 h and every 2 h to end of test.

#### After test pumping has ceased, record water level at same time intervals as in 3.7.4.3 until static water level is reached.

#### Take temperature of water discharged from well during test pumping at intervals of 1 h.

### When test pumping is to be conducted after disinfection, swab with strong chlorine solution parts of test pump coming into contact with well water prior to start of test pumping.

### Should test pump fail during pump test, allow water to reach static level prior to recommencing test. No payment will be made for pump time prior to such failure.

### Do not allow pumping level to fall below elevation 2.0 m above top of well screen.

## WATER SAMPLING

### Obtain 4 (four) water samples from well during test pumping for analysis by Owner for suspended solids.

### Supply field turbidity metre. Measure and record water turbidity every 30 minutes during pumping.

### During final test pumping, obtain two (2) samples of water for bacterialogical analysis and one sample for chemical analysis 1/2 h after start of test pumping and again during last 15 min of test pumping. Total of 6 samples.

### Submit samples to approved laboratory.

END OF SECTION