# GENERAL

## SECTION INCLUDES

### Materials and installation for water mains, hydrants, valves, valve boxes, and valve chambers, including service connections.

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 78 00 - Closeout Submittals.

### Section 03 20 00 – Concrete Reforcing.

### Section 03 30 00 – Cast-in-Place Concrete.

### Section 31 23 33.01 – Excavating, Trenching and Backfilling.

## REFERENCES

### American National Standards Institute/American Water Works Association (ANSI/AWWA)

#### ANSI/AWWA B301, Liquid Chlorine.

#### ANSI/AWWA C104/A21.4, Cement-Mortar Lining for Ductile-Iron Pipe and Fittings for Water.

#### ANSI/AWWA C110/A21.10, Ductile-Iron and Gray Iron Fittings, 3 inch through 48 inch (75 mm through 1200 mm), for Water.

#### ANSI/AWWA C111/A21.11, Rubber-Gasket Joints for Ductile-Iron and Gray Iron Pressure Pipe and Fittings.

#### ANSI/AWWA C151/A21.51, Ductile-Iron Pipe, Centrifugally Cast, for Water.

#### ANSI/AWWA C153/A21.53, Ductile-Iron Compact Fittings for Water Service.

#### ANSI/AWWA C500, Metal-Seated Gate Valves for Water Supply Service (Includes Addendum C500a-95).

#### ANSI/AWWA C600, Installation of Ductile-Iron Water Mains, and Their Appurtenances.

#### ANSI/AWWA C651, Disinfecting Water Mains.

### American Society for Testing and Materials International, (ASTM)

#### ASTM A307, Standard Specification for Carbon Steel Bolts and Studs, 60,000 psi Tensile.

#### ASTM C117, Standard Test Method for Material Finer Than 75 [MU] m (No. 200) Sieve in Mineral Aggregates by Washing.

#### ASTM C136, Standard Method for Sieve Analysis of Fine and Coarse Aggregates.

#### ASTM C478M, Standard Specification for Precast Reinforced Concrete Manhole Sections, Metric.

#### ASTM D698, Standard Test Method for Laboratory Compaction Characteristics of Soil Using Standard Effort (12,400 ft-lbf/ft (600 kN-m/m3)).

### American Water Works Association (AWWA)/Manual of Practice

#### AWWA M17, Installation, Field Testing, and Maintenance of Fire Hydrants.

### Canadian General Standards Board (CGSB)

#### CAN/CGSB-8.1, Sieves, Testing, Woven Wire, Inch Series.

### Canadian Standards Association (CSA International)

#### CAN/CSA-A257 Series, Standards for Concrete Pipe.

#### CSA A3000, Cementitious Materials Compendium

#### CSA B137 Series, Thermoplastic Pressure Piping Compendium

#### CAN/CSA-G30.18, Billet Steel Bars for Concrete Reinforcement.

#### CAN/CSA-G164, Hot Dip Galvanizing of Irregularly Shaped Articles.

## SUBMITTALS

### Submit complete shop drawings and construction schedule for water mains 600 mm diameter and larger. Include method for installation of water main.

### Inform Owner of proposed source of bedding materials and provide access for sampling at least four (4) weeks prior to commencing work.

### Submit manufacturer's test data and certification that pipe materials meet requirements of this section at least four (4) weeks prior to beginning work. Include manufacturer's drawings, information and shop drawings where pertinent.

### Pipe certification to be on pipe.

## CLOSEOUT SUBMITTALS

### Provide record drawings, including directions for operating valves, list of equipment required to operate valves, details of pipe material, location of air and vacuum release valves, hydrant details, maintenance and operating instructions.

#### Include top of pipe, horizontal location of fittings and type, valves, valve boxes, valve chambers and hydrants.

## DELIVERY, STORAGE AND HANDLING

### Deliver, store and handle materials in accordance with Section 01 61 00 – Common Product Requirements.

## SCHEDULING OF WORK

### Schedule Work to minimize interruptions to existing services.

### Submit schedule of expected interruptions to Owner for approval and adhere to interruption schedule as approved by Owner.

### Notify Owner, building occupants, superintendent minimum of two (2) working days in advance of interruption in service.

### Notify fire department of any planned or accidental interruption of water supply to hydrants.

### Advise local police department of anticipated interference with movement of traffic.

### Provide "Out of Service" sign on hydrant not in use.

# PRODUCTS

## PIPE, JOINTS AND FITTINGS

### Ductile iron pipe: to ANSI/AWWA C151/A21.51, pressure class 350, cement mortar lined to ANSI/AWWA C104/A21.4,

### Joints and fittings for ductile iron pipe.

#### Joints:

##### Rubber gasket for mechanical pipe joints: to ANSI/AWWA C111/A21.11,

##### Bolts, nuts, hex head with washers: to ASTM A307, heavy series.

##### Ensure electrical conductivity across joints.

#### Fittings:

##### Mechanical joint cast iron and ductile iron fittings NPS 3 and larger: to ANSI/AWWA C110/A21.10,

##### Compact Fittings to ANSI/AWWA C153/A21.53,

#### Reinforced concrete pipe: to CAN/CSA A257.

##### Pipe joints: push-on joints with performance requirements to ANSI/AWWA C111/A21.11,

## VALVES AND VALVE BOXES

### Gate valves: to AWWA C500, Latest Edition, standard iron body, bronze mounted double disc valves with non-rising stems. Suitable for 1 Pa with mechanical joints.

### Valves to open counter clockwise and to be supplied with a square-sided operating nut, 51 mm to the side unless otherwise specified.

### Cast iron valve boxes: bituminous coated screw type adjustable over minimum of 450 mm complete with valve operating extension rod,  30 mm minimum diameter, 25 x 25  mm cross section, of such length that when set on valve operating nut, top of rod will not be more than 150 mm below cover. Top of box to be marked "WATER".

## VALVE CHAMBERS

### Concrete and reinforcing steel: to Section 03 30 00 - Cast-in-Place Concrete and Section 03 20 00 - Concrete Reinforcing.

### Precast concrete sections to ASTM C478M, Cast ladder rungs integral with unit; field installation not permitted.

### Jointing materials:

#### Manufacturer's rubber ring gaskets.

#### Mastic joint filler.

#### Combination of above types.

### Ladder rungs for valve chambers: 20 mm diameter deformed rail steel bars to CAN/CSA-G30.18, hot-dipped galvanized after fabrication to CAN/CSA-G164. Rungs to be safety pattern.

## PIPE BEDDING AND SURROUND MATERIAL

### Granular material to: Section 31 05 16 – Aggregates for Earthwork and following requirements:

#### Crushed or screened stone, gravel or sand.

#### Gradations to be within limits specified when tested to ASTM C136, and ASTM C117, Sieve sizes to CAN/CGSB-8.1,

#### Table:

| Sieve Designation | % Passing |
| --- | --- |
|  | Stone/Gravel | Gravel/Sand |
| 200 mm | - | - |
| 75 mm | - | - |
| 50 mm | - | - |
| 38.1 mm | - | - |
| 25 mm | 100 | - |
| 19 mm | - | - |
| 12.5 mm | 65-90 | 100 |
| 9.5 mm | - | - |
| 4.75 mm | 35-55 | 80-100 |
| 2.00 mm | - | 50- 90 |
| 0.425 mm | 10-25 | 10- 50 |
| 0.180 mm | - | - |
| 0.075 mm | 0- 8 | 0- 10 |

### Concrete mixes and materials required for bedding cradles, encasement, supports, thrust blocks: to Section 03 30 00 - Cast-in-Place Concrete. Minimum 28 day strength 25 Mpa.

## BACKFILL MATERIAL

### Type 3, in accordance with Section 31 23 33.01 - Excavating, Trenching and Backfilling.

## PIPE DISINFECTION

### Liquid chlorine to ANSI/AWWA B301, to disinfect water mains.

### Undertake disinfection of water mains in accordance with ANSI/AWWA C651,

## TOOLS AND EQUIPMENT

### Provide Owner with following tools:

#### One tee-handle operating keys for valves.

# EXECUTION

## PREPARATION

### Clean pipes, fittings, valves, hydrants, and appurtenances of accumulated debris and water before installation. Carefully inspect materials for defects to approval of Owner. Remove defective materials from site as directed by Owner.

## TRENCHING

### Do trenching work in accordance with Section 31 23 33.01 - Excavating Trenching and Backfilling.

### Trench depth to provide cover over pipe of not less than 3.05 m from finished grade or as indicated.

### Trench alignment and depth require Owner approval prior to placing bedding material and pipe.

## CONCRETE BEDDING AND ENCASEMENT

### Do concrete work in accordance with Section 03 30 00 - Cast-in-Place Concrete. Place concrete to details as indicated as directed by Owner.

### Pipe may be positioned on concrete blocks to facilitate placing of concrete. When necessary, rigidly anchor or weight pipe to prevent flotation when concrete is placed.

### Do not backfill over concrete within 24 hours after placing.

## GRANULAR BEDDING

### Place granular bedding material in uniform layers not exceeding 150 mm compacted thickness to depth of 150 mm below bottom of pipe.

### Do not place material in frozen condition.

### Shape bed true to grade to provide continuous uniform bearing surface for pipe.

### Shape transverse depressions in bedding as required to suit joints.

### Compact each layer full width of bed to at least 95% of corrected maximum density to ASTM D698.

### Fill authorized or unauthorized excavation below design elevation of bottom of specified bedding in accordance with Section 31 23 33.01 - Excavating Trenching and Backfilling with (compacted bedding material, compacted Type 3, fill lean mix concrete).

## PIPE INSTALLATION

### Terminate building water service 1.5 m inside building wall opposite point of connection to main. Install flange adapter and or coupling necessary for connection to building plumbing. If plumbing is already installed, make connection; otherwise cap or seal end of pipe and place temporary marker to locate pipe end.

### Lay pipes to manufacturer's standard instructions and specifications. Do not use blocks except as permitted in 3.3.2.

### Join pipes in accordance with manufacturer's recommendations.

### Handle pipe by methods recommended by pipe manufacturer. Do not use chains or cables passed through pipe bore so that weight of pipe bears on pipe ends.

### Lay pipes on prepared bed, true to line and grade. Ensure barrel of each pipe is in contact with shaped bed throughout its full length. Take up and replace defective pipe. Correct pipe which is not in true alignment or grade or pipe which shows differential settlement after installation greater than 10 mm in 3.0 m.

### Do not exceed permissible deflection at joints as recommended by pipe manufacturer.

### Keep jointing materials and installed pipe free of dirt and water and other foreign materials. Whenever work is stopped, install a removable watertight bulkhead at open end of last pipe laid to prevent entry of foreign materials.

### Position and join pipes with equipment and methods approved by Owner.

### Cut pipes in approved manner as recommended by pipe manufacturer, without damaging pipe or its coating and to leave smooth end at right angles to axis of pipe.

### Align pipes before jointing.

### Install gaskets to manufacturer's recommendations. Support pipes with hand slings or crane as required to minimize lateral pressure on gasket and maintain concentricity until gasket is properly positioned.

### Avoid displacing gasket or contaminating with dirt or other foreign material. Gaskets so disturbed or contaminated shall be removed, cleaned, lubricated and replaced before jointing is attempted again.

### Complete each joint before laying next length of pipe.

### Minimize deflection after joint has been made.

### Apply sufficient pressure in making joints to ensure that joint is completed to manufacturer's recommendations.

### Ensure completed joints are restrained by compacting bedding material alongside and over installed pipes or as otherwise approved by Owner.

### When stoppage of work occurs, block pipes in an approved manner to prevent creep during down time.

### Do not lay pipe on frozen bedding.

### Do hydrostatic and leakage test and have results approved by Owner before surrounding and covering joints and fittings with granular material.

### Backfill remainder of trench.

## VALVE CHAMBERS

### Use cast-in-place, precast units as approved by Owner.

### Construction units as indicated, plumb and centered over valve nut, true to alignment and grade, and not resting on pipe.

### Place reinforcing steel and miscellaneous metals required to be embedded in concrete to details indicated and in accordance with Section 03 30 00 – Cast-in-Place Concrete.

### Set bottom section of precast unit in bed of cement mortar and bond to bottom slab.

#### Make each successive joint watertight with approved rubber ring gaskets, mastic joint filler, cement mortar or combination thereof.

### Clean surplus mortar and joint compounds from interior surface of valve chambers as work progresses.

### Plug lifting holes with mastic compound.

### Place frame and cover on top section to elevation indicated. If adjustment is required use concrete ring.

### Clean valve chamber of debris and foreign materials, remove fins and sharp projections.

## VALVE INSTALLATION

### Install valves to manufacturer’s recommendations at locations as indicated.

### Support valves located in valve boxes or valve chambers by means of concrete blocks, located between valve and solid ground. Valves not to be supported by pipe.

## HYDRANTS

### Install hydrants at locations as indicated.

### Install hydrants in accordance with AWWA M17.

### Install gate valve and cast iron valve box on hydrant services leads as indicated.

### Set hydrants plumb, with hose outlets paralled with edge of pavement or curb line, with pumper connection facing roadway and with body flange set at elevation of 50mm above final grade.

### Place concrete thrust blocks as indicated and specified, ensuring that drain holes are unobstructed.

### Place appropriate sign on installed hydrants indicating whether or not they are in service during construction.

## THRUST BLOCKS AND RESTRAINED JOINTS

### Do concrete work in accordance with Section 03 30 00 - Cast-in-Place Concrete.

### Place concrete thrust blocks between valves, tees, plugs, caps, bends, changes in pipe diameter, reducers, hydrants and fittings and undisturbed ground as indicated or as directed by Owner.

### Keep joints and couplings free of concrete.

### Do not backfill over concrete within 24 hours after placing.

### For restrained joints: only use restrained joints approved by Owner.

## HYDROSTATIC AND LEAKAGE TESTING

### Do tests in accordance with ANSI/AWWA C600.

### Provide labour, equipment and materials required to perform hydrostatic and leakage tests hereinafter described.

### Notify Owner at least two (2) working days in advance of proposed tests. Perform tests in presence of Owner.

### Where section of system is provided with concrete thrust blocks, conduct tests at least 5 days after placing concrete or two (2) days if high early strength concrete is used.

### Test pipeline in sections not exceeding 365 m in length, unless otherwise authorized by Owner.

### Upon completion of pipe laying and after Owner has inspected work in place, surround and cover pipes between joints with approved granular material placed to dimensions indicated.

### Leave valves, joints and fittings exposed.

### When testing is done during freezing weather, protect hydrants, valves, joints and fittings from freezing.

### Strut and brace caps, bends, tees, and valves, to prevent movement when test pressure is applied.

### Open valves.

### Expel air from main by slowly filling main with potable water. Install corporation stops at high points in main where no air-vacuum release valves are installed. Remove stops after satisfactory completion of test and seal holes with plugs.

### Thoroughly examine exposed parts and correct for leakage as necessary.

### Apply hydrostatic test pressure of 1000 kPa based on elevation of lowest point in main and corrected to elevation of test gauge, for period of 1 hour.

### Examine exposed pipe, joints, fittings and appurtenances while system is under pressure.

### Remove joints, fittings and appurtenances found defective and replace with new sound material and make watertight.

### Repeat hydrostatic test until defects have been corrected.

### Define leakage as amount of water supplied from water storage tank in order to maintain test pressure for 2 h.

### Do not exceed allowable leakage of 0.03 L/mm diameter per 300 m of pipe, including lateral connections, per hour.

### Locate and repair defects if leakage is greater than amount specified.

### Repeat test until leakage is within specified allowance for full length of watermain.

### Co-ordinate test procedure with Owner and provide certification of test acceptance.

## PIPE SURROUND

### Upon completion of pipe laying and after Owner has inspected work in place, surround and cover pipes as indicated.

### Hand place surround material in uniform layers not exceeding 150 mm compacted thickness as indicated. Do not dump material within 1.00 m of pipe.

### Place layers uniformly and simultaneously on each side of pipe.

### Do not place material in frozen condition.

### Compact each layer from pipe invert to mid height of pipe to at least 95% maximum density to ASTM D698.

### Compact each layer from mid height of pipe to underside of backfill to at least 90 % of corrected maximum density to ASTM D698.

## BACKFILL

### Place backfill material, above pipe surround, in uniform layers not exceeding 150 mm compacted thickness up to grades as indicated.

### Do not place backfill in frozen condition.

### Under footings, parking area and walks, compact backfill to at least 95% maximum density to ASTM D698.

## HYDRANT FLOW TESTS

### Conduct flow tests on every hydrant to determine fire flows prior to painting hydrant caps and ports.

## PAINTING OF HYDRANTS

### After hydrant flow tests, paint caps and ports to meet colour selections approved by authority having jurisdiction.

## FLUSHING AND DISINFECTING

### Flushing and disinfecting operations shall be carried out by specialist contractor and witnessed by Owner. Notify Owner at least four (4) days in advance of proposed date when disinfecting operations will commence.

### Flush water mains through available outlets with a sufficient flow of potable water to produce velocity of 1.5 m/s, within pipe for minimum 10 minutes, or until foreign materials have been removed and flushed and water is clear.

### Flushing flows as follows: 38 L/s minimum.

### Provide connections and pumps for flushing as required.

### Open and close valves, hydrants and service connections to ensure thorough flushing.

### When flushing has been completed to satisfaction of Owner introduce a strong solution of chlorine as approved by Owner into watermain and ensure that it is distributed throughout entire system.

### Disinfect water mains.

### Rate of chlorine application to be proportional to rate of water entering pipe.

### Chlorine application to be close to point of filling water main and to occur at same time.

### Operate valves, hydrants and appurtenances while main contains chlorine solution.

### Flush line to remove chlorine solution after 24 hours.

### Measure chlorine residuals at extreme end of pipe-line being tested.

### Perform bacteriological tests on water main, after chlorine solution has been flushed out. Take samples daily for minimum of two days. Should contamination remain or recur during this period, repeat disinfecting procedure. Specialist contractor to submit certified copy of test results.

### Take water samples at hydrants and service connections, in suitable sequence, to test for chlorine residual.

### Co-ordinate flushing disinfection with Owner.

### Provide certification of test acceptance.

## SURFACE RESTORATION

### After installing and backfilling over water mains, restore surface to original condition as directed by Owner.

## QUALITY ASSURANCE

### Provide copies of all inspections and test results for Commissioning Manuals.

END OF SECTION