# GENERAL

## SECTION INCLUDES

### Materials and installation for precast concrete septic tanks.

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 31 05 16 – Aggregates for Earthwork.

### Section 31 23 33.01 - Excavating Trenching and Backfilling.

### Section 33 36 33 - Utility Drainage Fields

## REFERENCES

### American Society for Testing and Materials International, (ASTM)

#### ASTM C117, Standard Test Method for Material Finer Than 0.075 mm (No. 200) Sieve in Mineral Aggregates by Washing.

#### ASTM C136, Standard Method for Sieve Analysis of Fine and Coarse Aggregates.

#### ASTM D698, Standard Test Method for Laboratory Compaction Characteristics of Soil Using Standard Effort (12,400 ft-lbf/ft3 (600 kN-m/m3)).

### Canadian General Standards Board (CGSB)

#### CAN/CGSB-8.2, Sieves, Testing, Woven Wire, Metric.

### Canadian Standards Association, (CSA International)

#### CAN/CSA-A23.1/A23.2, Concrete Materials and Methods of Concrete Construction/Methods of Test for Concrete.

#### CAN/CSA-A23.4/A251, Precast Concrete-Materials and Construction/Qualification Code for Architectural and Structural Precast Concrete Products.

#### CAN/CSA-B66, Prefabricated Septic Tanks and Sewage Holding Tanks.

#### CSA B1800, Plastic Non-pressure Pipe Compendium – B1800 Series (Consists of B181.1, B181.2, B181.3, B181.5, B182.2, B182.4, B182.6, B182.7, B182.8 and B182.11).

##### CSA B182.2, PVC Sewer Pipe and Fittings (PSM Type).

## DESIGN REQUIREMENTS

### Design precast concrete septic tank in accordance with CAN/CSA-B66, and to carry handling stresses and indicated service loads.

### Tank to have minimum total working capacity as indicated.

## SUBMITTALS

### Shop drawings to indicate:

#### Design calculations for items designed by manufacturer.

#### Tables and bending diagrams of reinforcing steel.

#### Camber.

#### Formwork.

#### Finishing schedules.

#### Methods of handling and erection.

#### Storage facilities.

#### Openings, sleeves, inserts and related reinforcement.

## QUALIFICATIONS

### Manufacturers and erectors of precast concrete elements shall be certified by CSA as meeting requirements of CAN/CSA-A23.4/A251, for Category SC and SP products.

# PRODUCTS

## CONCRETE MIXES AND MATERIALS

### Concrete mixes and materials: to CAN/CSA-B66 and CAN/CSA-A23.1/A23.2.

### Use type 10 cement.

## MANUFACTURE

### Manufacture units in accordance with CAN/CSA-A23.4/A251, except where specified otherwise. Piping as indicated on drawings.

## FINISHES

### Finish tanks to commercial grade to CAN/CSA-A23.4/A251.

## SIPHON CHAMBER

### Siphon chamber to meet design requirements specified for septic tanks.

### Provide siphon chamber vents.

## ACCESS

### Provide access holes to surface to facilitate cleaning inspection.

## TANK BEDDING AND SURROUND MATERIAL

### Granular material to Section 31 05 16 – Aggregates for Earthwork and following requirements:

#### Crushed or screened stone, gravel or sand.

#### Gradations to be within limits specified when tested to ASTM C136 and ASTM C117. Sieve sizes to CAN/CGSB-8.2.

#### Table

| Sieve Designation | % Passing |
| --- | --- |
| 200 mm | - |
| 75 mm | - |
| 50 mm | - |
| 37.5 mm | - |
| 25 mm | - |
| 19 mm | - |
| 12.5 mm | 100 |
| 9.5 mm | - |
| 4.75 mm | 80-100 |
| 2.00 mm | 50- 90 |
| 0.425 mm | 10- 50 |
| 0.180 mm | - |
| 0.075 mm | 0- 10 |

## BACKFILL MATERIAL

### As indicated.

### Type 3, in accordance with Section 31 23 33.01 - Excavating, Trenching and Backfilling.

## MODULAR WALL SEALS

### Provide modular wall seals.

## EFFLUENT FILTER

### Consists of primary and secondary filter to permit removal of primary filter for servicing. Filter material to be non-corrosive PVC, ABS and polyethylene.

### Filter container complete with primary and secondary pull rods, inlet and outlet, leg bosses to accept either NPS 32 mm or 38 mm SCH 40 PVC pipe and septic tank riser with cover.

### Capacity: filter area, slot diameter and flow rate as indicated.

### Filters manifold together as indicated.

# EXECUTION

## INSTALLATION

### Place bedding and surround material in unfrozen condition.

### Do excavation in accordance with Section 31 23 33.01 - Excavating, Trenching and Backfilling.

### Place tank bedding material in accordance with details as indicated. Compact to 95% maximum dry density to ASTM D698.

### Make inlet and outlet joints of septic tank watertight, using modular wall seals.

### Conduct leakage test on septic tank in presence of Owner, before backfilling. Fill tank to level of effluent pipe, and allow to stand for 24 hours. Allowable leakage is zero.

### Do backfilling in accordance with Section 31 23 33.01 - Excavating, Trenching and Backfilling.

#### Compact to 90% maximum dry density to ASTM D698.

END OF SECTION