# GENERAL

## SECTION INCLUDES

### Materials and installation for trench type septic tank disposal fields.

## RELATED SECTIONS

### Section 01 33 00 - Submittal Procedures.

### Section 01 74 21 – Construction/Demolition Waste Management and Disposal.

### Section 31 05 16 – Aggregates for Earthwork.

### Section 31 23 33.01 - Excavating Trenching and Backfilling.

### Section 33 36 00 - Wastewater Utility Storage Tanks.

## REFERENCES

### American Society for Testing and Materials International, (ASTM)

#### ASTM C117, Standard Test Method for Material Finer Than 0.075 mm (No. 200) Sieve in Mineral Aggregates by Washing.

#### ASTM C136, Standard Method for Sieve Analysis of Fine and Coarse Aggregates.

#### ASTM D422, Standard Method for Particle-Size Analysis of Soils.

#### ASTM D4318, Standard Test Method for Liquid Limit, Plastic Limit and Plasticity Index of Soils.

### Canadian General Standards Board (CGSB)

#### CAN/CGSB-8.2, Sieves, Testing, Woven Wire, Metric.

### Canadian Standards Association (CSA International)

#### CSA B1800, Plastic Non-pressure Pipe Compendium - B1800 Series (Consists of B181.1, B181.2, B181.3, B181.5, B182.1, B182.2, B182.4, B182.6, B182.7, B182.8 and B182.11).

##### CSA B182.2, PVC Sewer Pipe and Fittings (PSM Type).

## SUBMITTALS

### Submit to Owner 20 kg samples of granular materials at least four (4) weeks prior to beginning Work.

### Submit to Owner copy of certification or licence of approved installers.

## QUALITY ASSURANCE

### Use certified, licenced installers who comply with local authority having jurisdiction.

# PRODUCTS

## GRANULAR MATERIALS

### Granular material to Section 31 05 16 – Aggregates for Earthwork and following requirements:

#### Pit run crushed or screened stone, gravel or sand.

#### Gradations to be within limits specified when tested to ASTM C136 and ASTM C117. Sieve sizes to CAN/CGSB-8.2.

#### Table

| Sieve |  | % Passing Designation |
| --- | --- | --- |
|  | Sand | Stone |
| 200 mm | - | - |
| 75 mm | - | - |
| 50 mm | - | - |
| 38.1 mm | - | - |
| 25 mm | - | 80-100 |
| 19 mm | - | 0-5 |
| 12.5 mm | 100 | - |
| 9.5 mm | - | - |
| 4.75 mm | 80-100 | - |
| 2.00 mm | 50-90 | - |
| 0.425 mm | 10-50 | - |
| 0.180 mm | - | - |
| 0.075 mm | 0-5 | - |

## IMPORTED FILTER MATERIAL

### Washed stone conforming to requirements of local authority having jurisdiction.

## PIPE FOR DISPOSAL FIELDS

### Straight PVC pipe and fittings to CAN/CSA-B182.2. Perforated or unperforated as indicated.

## DISTRIBUTION BOX

### Concrete: as indicated and to Section 33 36 00 - Wastewater Utility Storage Tanks.

## SOURCE QUALITY CONTROL

### If requested, provide Owner with three (3) certified copies of factory tests of pipe material.

# EXECUTION

## TRENCH TYPE DISPOSAL FIELD INSTALLATION

### Excavate to lines and depths as indicated and in accordance with Section 31 23 33.01 - Excavating, Trenching and Backfilling.

### Scarify trench base and walls under dry conditions.

### Obtain Owner’s approval to operate construction equipment across disposal field.

### Place minimum 150 mm of stone material in bottom of trench.

### Install distribution box between septic tank and absorption trenches. Installation to be water-tight construction.

### Distribution box: set level as indicated. Provide access with removable cover for inspection of distribution box.

### Connect lengths and place distribution pipe on stone material as indicated and cover with minimum 50 mm of stone material.

### Connect each distribution pipe individually to distribution box.

### Cap or plug free ends of distribution lines.

### Maintain pipe elevations within 5 mm of inverts indicated.

### Do not backfill trenches until pipe grade and alignment have been approved by Owner and authority having jurisdiction.

### Backfill trenching with material as indicated. Material to be approved by Owner. Do not compact. Overfill to allow for settlement.

END OF SECTION