# GENERAL

## REFERENCE STANDARDS

### Do the work in accordance with Canadian Plumbing Code and local authority having jurisdiction except where specified otherwise.

## SHOP DRAWINGS

### Submit shop drawings in accordance with Section 01 33 00 – Submittal Procedures.

### Indicate dimensions, RSI-values, construction details and materials for the following:

#### All piping and fittings.

## PRODUCT DATA

### Submit product data in accordance with Section 01 33 00 – Submittal Procedures.

## MAINTENANCE DATA

### Provide maintenance data for incorporation into manual specified in Section 01 33 00 – Submittal Procedures.

### Data to include:

#### Description of plumbing specialties and accessories, giving manufacturers name, type, model, year and capacity.

#### Details of operation, servicing and maintenance.

#### Recommended spare parts list.

# PRODUCTS

## Exterior Buried Underground Hydronic Piping

### General: Piping to be flexible corrosion proof plastic pre-insulated with outer jacket.

### Carrier Pipe: Dual cross linked PEX pipes suitable for temperatures up to 96°C.

### Insulation: Insulation to be factory applied closed cell polyurethane at a thickness of 32 mm.

### Jacket: The outer protective jacket to be corrugated seamless polyethylene completely encompassing the insulation and providing a moisture barrier designed for H-20 loading at a burial depth of only 600 mm.

### Fittings: All fittings to be by the same manufacturer as the piping system. Fittings to be brass and installed in accordance with manufacturers instructions.

### End Seals:  All exposed insulation ends to be sealed with polyethylene end seals.

# EXECUTION

## INSTALLATION

### Install all piping, fittings, valves and specialties in accordance with the manufacturer's recommendations.

### Test all piping to 1.5 times working pressure prior to burial.

### Backfill in accordance with manufacturers instructions.

END OF SECTION